## Answer Sheet
Parsons-GHD USEPA Asset Management Workshops 2003
This workbook is copyrighted by Parsons/GHD. It is intended for the use of and licensed for use by utility staff and public officials. Feel free to modify it to fit your organization, but please assure proper citation.
Asset Hierarchy |  |  |  |  | Installed Date | Asset Class | Original Cost | Estimated Effective Life | Annual Dep | Accum Dep | Condition Rating | Residual Physical Life | % Asset Consumed (Physical) | Backup Reduction (Redundancy) | Probability of Failure | Consequence of Failure | BRE Rating | Future Maintenance % Change | Residual Economic Life | Renewal Strategy | Cost of Renewal Option | Recommended Renewal Date | Comments | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023
Level 1 | Level 2 | Level 3 | Level 4 | Level 5 | Year |  | $ | Years | $ | $ | 1 to 5 |  | % | % | Rating | 1 to 10 |  | % | Use your |  | $ |  | Justify the renewal choice
Name | Name | Name | Name | Name |  | Sheet B | Act or Est | Sheet B | Calculated | Calculated | Sheet A | Sheet B | Calculated | Sheet D | Calculated | Sheet C | Calculated | Sheet E | judgement | Sheet F |  | Calculated
Sanitation System
Disposal System
Treatment Plants
Collection Systems
Sewer Mains
Pump Station
Incoming Sewer
|  |  |  | Pipes | 1963 | 3 | 4250 | 100 | 42.5 | 1700 | 4 | 40 | 60% | 0% | 6 | 5 | 30 | 125% | 50 | 5 | 25000 | 2045
|  |  |  | Manhole | 1963 | 3 | 1360 | 100 | 13.6 | 544 | 3 | 60 | 40% | 0% | 4 | 5 | 20 | 100% | 40 | 5 | 8000 | 2045
|  |  |  | Influent Gate Valve | 1963 | 5 | 442 | 30 | 14.7333 | 589.3333 | 5 | 6 | 80% | 0% | 8 | 5 | 40 | 150% | 10 | 7 | 2600 | 2011 |  | 2011: 2600
Incoming Power
|  |  |  | Pole & Transformer | 1950 | 7 | 2550 | 30 | 85 | 4505 | 1 | 30 | 0% | 0% | 0 | 5 | 0 | 75% | 40 | 7 | 15000 | 2035
|  |  |  | Connection | 1963 | 7 | 340 | 30 | 11.3333 | 453.3333 | 1 | 30 | 0% | 0% | 0 | 5 | 0 | 50% | 35 | 7 | 2000 | 2035
Control system
|  |  |  | Incoming Telephone | 1963 | 8 | 85 | 25 | 3.4 | 136 | 4 | 10 | 60% | 0% | 6 | 5 | 30 | 50% | 30 | 6 | 500 | 2015 |  | 2015: 500
|  |  |  | PLC | 1983 | 8 | 8600 | 25 | 344 | 6880 | 4 | 10 | 60% | 0% | 6 | 2 | 12 | 150% | 2 | 8 | 5000 | 2007 |  | 2007: 5000
|  |  |  | Manual controls | 1963 | 8 | 170 | 25 | 6.8 | 272 | 3 | 15 | 40% | 100% | 0 | 2 | 0 | 125% | 15 | 7 | 1000 | 2020 |  | 2020: 1000
|  |  |  | Connections | 1963 | 8 | 425 | 25 | 17 | 680 | 3 | 15 | 40% | 0% | 4 | 3 | 12 | 125% | 20 | 7 | 2500 | 2020 |  | 2020: 2500
Land & Improvemnts.
|  |  |  | Land | 1950 | 10 | 630 | 300 | 2.1 | 111.3 | 1 |  | 100% | 0% | 10 | 1 | 10 | 50% | 100 | 1 | 0 | 2105
|  |  |  | Access Road | 1963 | 1 | 12500 | 75 | 166.6667 | 6666.6667 | 5 | 15 | 80% | 0% | 8 | 1 | 8 | 125% | 15 | 2 | 2400 | 2020 |  | 2020: 2400
|  |  |  | Landscaping | 1963 | 1 | 1275 | 75 | 17 | 680 | 4 | 30 | 60% | 0% | 6 | 1 | 6 | 150% | 2 | 7 | 7500 | 2007 |  | 2007: 7500
|  |  |  | Security fence | 1963 | 1 | 425 | 75 | 5.6667 | 226.6667 | 4 | 30 | 60% | 0% | 6 | 3 | 18 | 125% | 5 | 5 | 2500 | 2010 |  | 2010: 2500
Sub Structure
|  |  |  | Cassion Outer | 1963 | 1 | 30600 | 75 | 408 | 16320 | 3 | 45 | 40% | 0% | 4 | 5 | 20 | 75% | 50 | 5 | 180000 | 2050
|  |  |  | Upper Floor | 1963 | 1 | 4250 | 75 | 56.6667 | 2266.6667 | 4 | 30 | 60% | 0% | 6 | 4 | 24 | 50% | 50 | 5 | 25000 | 2035
|  |  |  | Dry well | 1963 | 1 | 6800 | 75 | 90.6667 | 3626.6667 | 3 | 45 | 40% | 0% | 4 | 5 | 20 | 50% | 50 | 5 | 40000 | 2050
|  |  |  | Landings and Stairs | 1963 | 9 | 4250 | 30 | 141.6667 | 5666.6667 | 5 | 6 | 80% | 0% | 8 | 3 | 24 | 100% | 8 | 5 | 25000 | 2011 |  | 2011: 25000
|  |  |  | Wet Well | 1963 | 1 | 5100 | 75 | 68 | 2720 | 3 | 45 | 40% | 0% | 4 | 4 | 16 | 75% | 25 | 5 | 30000 | 2030
|  |  |  | Shaped floor | 1963 | 1 | 850 | 75 | 11.3333 | 453.3333 | 4 | 30 | 60% | 0% | 6 | 1 | 6 | 100% | 12 | 5 | 5000 | 2017 |  | 2017: 5000
|  |  |  | Sump pump | 1963 | 1 | 595 | 75 | 7.9333 | 317.3333 | 5 | 15 | 80% | 100% | 0 | 2 | 0 | 150% | 4 | 7 | 3500 | 2009 |  | 2009: 3500
Pumps
|  |  |  | Drive shafts | 1963 | 4 | 4250 | 40 | 106.25 | 4250 | 3 | 24 | 40% | 100% | 0 | 5 | 0 | 150% | 10 | 7 | 25000 | 2015 |  | 2015: 25000
|  |  |  | Pumps | 1963 | 4 | 5100 | 40 | 127.5 | 5100 | 4 | 16 | 60% | 100% | 0 | 5 | 0 | 150% | 10 | 7 | 30000 | 2015 |  | 2015: 30000
|  |  |  | Motors | 1963 | 6 | 4250 | 35 | 121.4286 | 4857.1429 | 4 | 14 | 60% | 100% | 0 | 5 | 0 | 150% | 5 | 7 | 25000 | 2010 |  | 2010: 25000
Electrics
|  |  |  | Meters & Fuses | 1963 | 7 | 1275 | 30 | 42.5 | 1700 | 4 | 12 | 60% | 0% | 6 | 5 | 30 | 125% | 30 | 7 | 7500 | 2017 |  | 2017: 7500
|  |  |  | Switchboard | 1963 | 7 | 5780 | 30 | 192.6667 | 7706.6667 | 4 | 12 | 60% | 0% | 6 | 5 | 30 | 150% | 12 | 5 | 34000 | 2017 |  | 2017: 34000
|  |  |  | Pump Starters | 1963 | 7 | 680 | 30 | 22.6667 | 906.6667 | 5 | 6 | 80% | 0% | 8 | 3 | 24 | 150% | 10 | 7 | 4000 | 2011 |  | 2011: 4000
|  |  |  | Emergency connect. | 2004 | 7 | 2210 | 30 | 73.6667 | -73.6667 | 0 |  | 100% |  | 10 |  |  | 100% | 1 | 12 | 13000 | 2006 |  | 2006: 13000
|  |  |  | Alarms / General L& P. | 1963 | 7 | 595 | 30 | 19.8333 | 793.3333 | 4 | 12 | 60% | 0% | 6 | 3 | 18 | 150% | 8 | 7 | 3500 | 2013 |  | 2013: 3500
Force Main
|  |  |  | Pipes | 1963 | 2 | 11560 | 60 | 192.6667 | 7706.6667 | 4 | 24 | 60% | 0% | 6 | 5 | 30 | 150% | 15 | 5 | 68000 | 2020 |  | 2020: 68000
|  |  |  | Valves(check& gate) | 1963 | 5 | 1105 | 30 | 36.8333 | 1473.3333 | 5 | 6 | 80% | 0% | 8 | 4 | 32 | 200% | 10 | 7 | 6500 | 2011 |  | 2011: 6500
Superstructure
|  |  |  | Walls | 1963 | 9 | 3400 | 30 | 113.3333 | 4533.3333 | 3 | 18 | 40% | 0% | 4 | 2 | 8 | 125% | 35 | 5 | 20000 | 2023 |  | 2023: 20000
|  |  |  | Roof | 1963 | 9 | 1445 | 30 | 48.1667 | 1926.6667 | 5 | 6 | 80% | 0% | 8 | 3 | 24 | 150% | 8 | 6 | 8500 | 2011 |  | 2011: 8500
|  |  |  | Services | 1963 | 9 | 510 | 30 | 17 | 680 | 4 | 12 | 60% | 50% | 3 | 2 | 6 | 150% | 30 | 7 | 3000 | 2017 |  | 2017: 3000
|  |  |  | Roller door | 1963 | 9 | 408 | 30 | 13.6 | 544 | 4 | 12 | 60% | 0% | 6 | 2 | 12 | 125% | 10 | 7 | 2400 | 2015 |  | 2015: 2400
|  |  |  | Gantry Crane | 1963 | 9 | 2040 | 30 | 68 | 2720 | 4 | 12 | 60% | 0% | 6 | 2 | 12 | 100% | 25 | 5 | 12000 | 2017 |  | 2017: 12000
[7 empty] | 130105 |  | 2708.0786 | 99527.8095 | [10 empty] | 644900 |  |  | 0 | 0 | 13000 | 12500 | 0 | 3500 | 27500 | 46600 | 0 | 3500 | 0 | 57900 | 0 | 61500 | 0 | 0 | 73900 | 0 | 0 | 20000
[21 empty] | 525000 |  |  | 2004: 180441.2513
[24 empty] | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626 | 9022.0626
[24 empty] | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708 | 2708
Note on U9: Renewal Strategy: 1- Staus quo 2 Increase Maintenance 3 Operate differently 4 Repair only 5 Refurbish or rehabilitate 6 Replace with similar asset 7 Replace with improved asset 8 Reduce the cause of failure 9 Use demand management 10 Pay rebate to customers 11 Reduce the level of service 12 Construct a new asset
Note on S9: Future Maintenance Change (%): 1 Status Quo 100% 2 Slightly higher 125% 3 Considerably higher 150% 4 Significantly Higher 200% 5 Reduce Slightly 75% 6 Reduce moderately 50% 7 Reduced significantly 25%
Note on Q9: Consequence of Failure (CoF): CoF Rating Description % Affected Level 1 Minor Component Failure 0-50% Child Asset 2 Major Component Failure 50-100% Child Asset 3 Major Asset 0-50% Asset 4 Major asset 50-100% Asset 5 Multiple Asset Failure 0-50% Facility /Sub-System 6 Major Facilty Failure 50-100% Facility /Sub-System 7 Minor Sanitory System Failure 20-40% Total System 8 Medium System failure 40-60% Total System 10 Intermediate System Failure 60-75% Total System 15 Significant system Failure 75-90% Total System 20 Total System Failure 90-100% Total System
Note on T8: Residual Economic Life: Compare the key issues in relation to the asset component :. 1 The BRE (Column N) 2 The change in maintenance costs (Column E) 3 The residual physical life ( column I) Now choose a residual economic life based on your best assessment .
Note on V8: Cost of Renewal Option: For this column you need to use your best valued judgement …use the best information you can get including : engineering estimators, manufacturers & agents & your knowledgeable staff & construction contractors ( ask them for a price)
Note on W8: Recommended Renewal Date: This is calculated by the spreadsheet, setting the year based on your 'residual economic life' (see Column T)
Note on X8: GHD: Please record any comments here that backs up your decision re strategy and the date for same ..
Note on R8: Business Risk Exposure (BRE): This column is calculated by the spreadsheet .. It multiplies the probability of failure (% of life consumed) by the consequence of failure you have determined for each component.
Note on N8: % Asset Comsumed (Physical): This is calculated by the spreadsheet taking the effective life that you have identified for the individual components from a condition perspective.. (see next step documents for optimising your verification of these valued judgements ('delphi group')) ..
Note on P8: Probability of Failure (PoF): This is calculted by the software. It is just the % effective life consumed (Column J) being used as a number equal to this divided by 10,, just to give a quick figure …This is then modified by the back up that we have for some assets & components.
Note on O8: Redundancy: Make allowance for the Level of Redundancy .Reduce PoF by: 50% Backup 50% 100% Backup 90% 200% Secondary Backup 98%
Note on M8: Residual Physical Life: This is done by following the chart below and shown on sheet B at the bottom of the spreadsheet. This is for a guide only… We want your expert group to really try and judge the condition and the residual physical life. You need to do this realistically ..and HONESTLY. Try not to be pessimistic .. Use the chart to understand the residual lives that we found to be correct after 15 years of doing this ..so use them to help justify the figures you adopt Effective Lives (Years) Condition Rating / Residual Life Asset Type Average Effective Lives 1 2 3 4 5 Civil Structures 75 75 60 45 30 15 Pressure Pipe work 60 60 48 36 24 12 Sewers – Gravity Pipe work. 100 100 80 60 40 20 Mechanical 40 40 32 24 16 8 Electrical Motors (large) 35 35 28 21 14 7 Other Electrical 30 30 24 18 12 6 Controls 25 25 20 15 10 5 Building Assets 60 60 48 36 24 12
Note on L8: Condition Rating: Insert your best assessment of the current condition of your assets using the following Basic condition score : Condition Assessment Condition Rating Description Maintenance Level Degree of Replacement 0 NEW Normal 0% 1 PERFECT/EXCELLENT CONDITION Normal 0% 2 MINOR DEFECTS ONLY Minor 5% 3 BACKLOG MAINTENANCE REQUIRED Significant 10-20% 4 REQUIRES MAJOR RENEWAL Renew 20-40% 5 ASSET ALMOST UNSERVICEABLE Replace >50%
Note on I8: Estimated Effective Life: (This is just a starting point) Effective Lives (Years) Asset Type Average Effective Lives Civil Structures 75 Pressure Pipe work 60 Sewers – Gravity Pipe work. 100 Mechanical 40 Electrical Motors (large) 35 Other Electrical 30 Controls 25 Building Assets 60
Note on F8: Installed Date: Set the date you believe the asset was first put into service. Don't b e too concerned about this as it doesn't matter a lot. Eventually .. It is just used to get us started
Note on G8: Asset Classes: 1 Civil 2 Pressure Pipework 3 Sewers 4 Pumps 5 Valves 6 Motors 7 Electrical 8 Controls 9 Building Assets 10 Land
Note on H8: Original Cost: In this case, these costs were estimated using current renewal/replacement costs deflated back to year of acquisition using a construction CPI.
Note on J8: Annual Depreciation: Straight-line depreciation is used here. More accurate "exponential" curves should be considered.
Note on K8: Accumulated Depreciaition: The sum of each year's depreciation expense since installation of the asset - "what we have expensed to date"

## A - Condition
Condition Assessment
Condition Rating | Description | Maintenance Level | Degree of Replacement
0 | NEW | Normal | 0%
1 | PERFECT/EXCELLENT CONDITION | Normal | 0%
2 | MINOR DEFECTS ONLY | Minor | 5%
3 | BACKLOG MAINTENANCE REQUIRED | Significant | 10-20%
4 | REQUIRES MAJOR RENEWAL | Renew | 20-40%
5 | ASSET ALMOST UNSERVICEABLE | Replace | >50%

## B - Residual Lives
| Effective Lives (Years) |  | Condition Rating / Residual Life
Class | Asset Type | Effective Lives | 1 | 2 | 3 | 4 | 5
1 | Civil | 75 | 75 | 60 | 45 | 30 | 15
2 | Pressure Pipework | 60 | 60 | 48 | 36 | 24 | 12
3 | Sewers | 100 | 100 | 80 | 60 | 40 | 20
4 | Pumps | 40 | 40 | 32 | 24 | 16 | 8
5 | Valves | 30 | 30 | 24 | 18 | 12 | 6
6 | Motors | 35 | 35 | 28 | 21 | 14 | 7
7 | Electrical | 30 | 30 | 24 | 18 | 12 | 6
8 | Controls | 25 | 25 | 20 | 15 | 10 | 5
9 | Building Assets | 30 | 30 | 24 | 18 | 12 | 6
10 | Land | 300 | 300 | 300 | 300 | 300 | 300

## C - Consequence of Failure
Consequence of Failure
CoF Rating | Description | % Affected | Level
1 | Minor Component Failure | 0-25% | Asset
2 | Major Component Failure | 25-50% | Asset
3 | Major Asset | 0-25% | Asset
4 | Multiple Asset Failure | 25-50% | Facility / Sub-System
5 | Major Facilty Failure | 50-100% | Facility
6 | Minor Sanitory System Failure | 20-40% | Total System
7 | Medium | 40-60% | Total System
8 | Intermediate | 60-80% | Total System
9 | Significant | 80-90% | Total System
10 | Total | 90-100% | Total System

## D - Probabilty of Failure
Probability of Failure
% of Effective Life Consumed | PoF Rating
0% | 1
10% | 2
20% | 3
30% | 4
40% | 5
50% | 6
60% | 7
70% | 8
80% | 9
90% | 10
Don't Forget Redundancy!
Level of Redundancy | Reduce PoF by:
50% Backup | 50%
100% Backup | 90%
200% Secondary Backup | 98%

## E - Maintenance Costs
Impact on Future Maintenance Costs
Rating | Description | Impact
1 | Status Quo | 100%
2 | Higher | 125%
3 | Considerably Higher | 150%
4 | Significantly Higher | 400%
5 | Reduced Slightly | 75%
6 | Reduced Significantly | 50%

## F - Renewal Strategies
Renewal Strategies
Option | Description | Type
1 | Continue with Status Quo | Non-Capital
2 | Increase Maintenance | Non-Capital
3 | Operated Differently | Non-Capital
4 | Repair | Capital
5 | Complete Significant Overhaul | Capital
6 | Replace Asset with Similar | Capital
7 | Replace with Improved Asset | Capital
8 | Complete Cause Reduction (stop the failure) | Capital
9 | Use Demand Management | Non-Asset
10 | Pay rebate to effected customers | Non-Asset
11 | Reduce Levels of Service | Non-Asset
12 | Install new asset | Capital